 INSTRUCTIONS FOR COMPLETING THE MONTHLY OPERATING LOG (MOL) 

MONTHLY UVT ANALYZER CALIBRATION LOG
INSTRUCTIONS FOR COMPLETING LOG:  
This log must be completed to document compliance with UVT analyzer calibration requirements of OAC Rule 3745-81-68(N)(4)(c).  This log must be completed for each UVT analyzer for each month and must be available for review upon request.  Online UVT analyzers are required to be calibrated at least weekly in accordance with OAC Rule 3745-81-68 (N)(4)(c).  The weekly calibrations for each UVT analyzer must be done using a certified spectrophotometer in the lab and results must be documented on this log.  Handheld UVT calibrations are not required to be recorded or documented.

Systems may complete the log at the time the UVT analyzer is calibrated or may enter data for the entire month, at the end of the month, if data is recorded in another location. 
PUBLIC WATER SYSTEM INFORMATION:
PWS Name:  Print or type name of public water system (PWS)

STU Name:  Print or type source treatment unit (STU) name.

PWSID#:  Enter the PWS ID number.

STUID#:  Enter the STU ID number.

Reporting Period:  Enter month and year in which data was collected.

UVT Analyzer Number:  Enter the UVT analyzer number for the unit this log is being completed for.

The following correspond to each of the columns in the table entitled “UVT Analyzer Calibration Report”.

Date:  Enter the date of the UVT analyzer is calibrated.
On-line Reading (%) [A]:  Enter the value obtained from the readout on the UVT analyzer.

Grab Sample Result (%) [B]:  Collect a grab sample and analyze the sample for UVT.  Record the value in this column.
Difference (%) ([A]-[B]): Calculate the difference between the on-line reading and the grab sample result.  Record the difference in this column.
Difference < 2% UVT? (Y/N):  If the difference is less than 2%, enter yes.  If the difference is equal to or greater than 2%, enter no.  
The following correspond to the “Certification” section of the form:

All calibration checks were within the acceptable tolerance during this month.  Check this box if all calibration checks were within the acceptable tolerance during this month.

Recalibration was required and is documented below. Check this box if the UVT analyzer was required to be recalibrated.  

On-site calibration.  Check this box if the UVT analyzer was calibrated on site.

Manufacturer Calibration.  Check this box if the UVT analyzer was sent to the manufacturer to be recalibrated.

The following correspond to each of the columns in the table entitled “UVT Analyzer Calibration”:

On-site or manufacturer calibration?:  If the UVT analyzer was calibrated on-site, enter “on-site.”  If the UVT analyzer was sent to the manufacturer for calibration, enter “manufacturer.”  If the UVT analyzer was calibrated on site and also was sent to the manufacturer, enter “both.”
H:\Engineering\Judy Stottsberry\JStottsb\LT2\FINAL MORS FOR LT2\MOL UVT analyzer calibration instructions.doc
