## README
ODOT ARC FLASH CALCULATION SPREADSHEET (Revised 10-28-21)
Stamp Field:
This analysis shall be performerd by a registered professional engineer.
Signature:
Date:
Organization:
LOCATION DATA
County/Route/Section:
Log point:
Address (if applicable):
Date of Fieldwork (if applic.):
Meter Number:
Location Sketch (add supporting documents as necessary on attached page)
DISCLAIMER MISSING

## Data Entry
Arc Flash Analysis Calculator for Proper PPE Requirements
Instructions: Enter data in highlighted fields to conduct an Arc Flash Analysis
| 1. Choose Phase (use dropdown menu): | 1-phase
| 2. Total kVA nameplate rating: | 25 | kVA
| 3. % Impedance (from nameplate): | 1.1
| 4. Choose Cable size from XFMR secondary to point of fault (use dropdown menu): | 6 | AWG
| 5. Distance from XFMR secondary to point of fault (feet): | 120 | feet
| 6. Base Voltage line-to-line (secondary): | 240 | V
| 7. # of Parallel Conductors Installed: | 1
| 8. Characteristic gap between conductors (13mm for ODOT Lighting and Signals): | 13 | mm
| 9. Open or boxed conductors (use dropdown menu): | boxed
| 10. Grounded or Ungrounded/High-R Grounded System (use dropdown menu): | grounded
| 11. Arcing Time from fuse or CB (use 2.0 sec. if unknown and power service ≤ 167 kVA, otherwise consult with power company): | 2 | seconds
| 12. Working Distance of person doing LIVE WORK: | 400 | mm
| 13. Calculation Factor per IEEE 1584-2002 9.11.3 (default = 1.50): | 1.5
Note:
1. The bolted fault current calculations were obtained from the electrical plan review
published by Cooper-Bussmann in November 2002.
2. The arcing current and incident energy calculations were obtained from IEEE Std. 1584-2002 "IEEE Guide for Performing Arc-Flash Hazard
Calculations."

## Results
Results: Arc Flash Analysis Calculator for Determining Appropriate PPE
Instructions: Enter data in Highlighted Fields to calculate the bolted fault current, arcing current and incident energy.
| Choose Phase (use dropdown menu): |  |  |  | Total kVA nameplate rating: |  |  |  | % Impedance (from Nameplate): |  |  |  | Choose Cable size from XFMR secondary to point of fault:
| 1-phase |  |  |  | 25 |  |  | kVA |  | 1.1 |  |  |  | 6 |  | AWG
| Distance from XFMR secondary to point of fault (feet): | [5 empty] | Base Voltage line-to-line (secondary): |  |  |  |  | # of Parallel Conductors Installed:
|  | 120 |  | feet |  |  |  | 240 |  | V |  |  | 1
| Characteristic gap between conductors (13mm for ODOT Lighting and Signals): | [7 empty] | Open or boxed conductors: |  |  |  | Grounded or Ungrounded/High-R Grounded System:
|  |  | 13 |  | mm |  |  |  | boxed |  |  |  |  | grounded
| Arcing Time from fuse or CB (use 0.2 if unknown): | [5 empty] | Working Distance of person doing LIVE WORK:
|  | 2 |  | seconds |  |  |  | 400 |  | mm
| Bolted Fault Current at XFMR Secondary is | [7 empty] | 10522 |  | A | line-line |  | and | 15782.8 |  | A | line-neutral.
| Bolted Fault Current at point of fault is | [6 empty] | 1971 | A | line-line |  | and | 1126.0 |  | A | line-neutral.
| The Arcing Current is |  |  |  | 1.0899 | kA | line-line |  | and | 0.6893 | kA | line-neutral.
| The Incident Energy is |  |  |  | 12.7906 | cal/cm^2 |  | line-line and |  | 7.7946 | cal/cm^2 |  | line-neutral.
| The Hazard Risk Category according to the Incident Energy is | [10 empty] | 3

## Calcs
The calculations and values contained below are all from the "Electrical Plan Review" PDF that is located on the Referenced PDFs sheet(referenced PDFs sheet has been removed). | [7 empty] | The calculations and values contained below are all from "IEEE 1584-2002" that is located on the Referenced PDFs sheet(referenced PDFs sheet has been removed).
3-phase |  | 6 | C= | 2425 | n= | 1 | References:
1-phase | [7 empty] | open | K= | -0.097 |  | 0.662
[8 empty] | boxed | K1= | -0.555 |  | 0.0966
step 1: full load current |  |  | 104.1667 | A |  |  | This value is obtained from Step 1 on Page 7. It will change depending on if the system is 1Ø or 3Ø. | grounded | K2= | -0.113 |  | 0.000526
[8 empty] | ungrounded/High-R Grounded | Cf= | 1.5 |  | 0.5588
step 2: transf. multiplier |  |  | 101.0101 |  |  |  | This value is obtained from Step 2 on Page 7. It is dependent upon the transformer percent impedance. |  | V= | 240 | l-l | -0.00304
[9 empty] | V= | 120 | l-n
step 3: bolted fault current |  |  | 10521.8855 | A (line to line) |  |  | The top value is obtained from Step 3 on Page 7. It is obtained by multiplying the full load current by the transformer multiplier. The bottom value is only used for 1Ø systems and is obtained by multiplying the top value by 1.5(the justification for this is included in Note 2 located at the bottom of Page 7.
| at tranformer |  | 15782.8283 | A (line to neutral) for 1-phase only |  |  |  | Formula 5.2
[9 empty] | Arcing Current |  | (for 1000 V and lower systems)
step 4: | find "f" factor |  |  | (for 3-phase fault) |  |  | The "f" factor is obtained from Step 4 on Page 7. There are three separate equatons depending on the fault and the phase of the system. The values used to obtain the "f" factor are both referenced and obtained from user input. |  | #VALUE! | L-L | 0.19505 | 0.034118 | L-N
|  |  | 4.3389 | (for 1-phase line-to-line fault) |  |  |  |  | 0.023184 |  | 0.023184 | 0.011592
|  |  | 13.0168 | (for 1-phase line-to-neutral fault) |  |  |  |  | 0.006838 |  | 0.006838 | 0.006838
[9 empty] | #VALUE! |  | 0.039515 | 0.0034559
step 5: find multiplier |  |  |  | (for 3-phase fault) |  |  | The multiplier is obtained from Step 5 on Page 7. The multiplier values are dependent upon the "f" factor for each phase and fault location. |  | #VALUE! |  | -0.1302 | -0.1206
|  |  | 0.1873 | (for 1-phase line-to-line fault) |  |  |  |  | -0.097 |  | -0.097 | -0.097
|  |  | 0.071343 | (for 1-phase line-to-neutral fault) | [9 empty] | (for 1 to 15 kV systems)
[8 empty] | log(Ia)= | #VALUE! |  | 0.037384 | -0.16159 |  | #VALUE! | 0.29365 | 0.054681
step 6: | bolted fault current |  |  | (for 3-phase fault) |  |  | The bolted fault current at the point of fault is obtained from Step 6 on Page 7. It is calculated by multiplying the transformer let-through short-circuit current by the multiplier for each particular phase and location of fault. | Ia= | #VALUE! |  | 1.0899 | 0.6893 |  | #VALUE! | 1.9663 | 1.1342
| at point of fault |  | 1970.7884 | (for 1-phase line-to-line fault)
|  |  | 1125.9964 | (for 1-phase line-to-neutral fault) |  |  |  | Formula 5.3
Incident Energy
[9 empty] | #VALUE! |  | 0.040412 | -0.17468 |  | #VALUE! | 0.31744 | 0.05911
[9 empty] | 0.0143 |  | 0.0143 | 0.0143 |  | 0.0143 | 0.0143 | 0.0143
The values in the "C Values fo Conductors" table on the right are from Table 2 on Page 8. |  |  | C values for Conductors | [5 empty] | Normalized Incident Energy
|  |  | 14 | 389 |  |  |  | log(En) | #VALUE! |  | -0.61329 | -0.82838 |  | #VALUE! | -0.33626 | -0.59459
|  |  | 12 | 617 |  |  |  | En | #VALUE! |  | 0.24362 | 0.14846 | (J/cm^2) | #VALUE! | 0.46104 | 0.25434
|  |  | 10 | 981 |  |  |  | En | #VALUE! |  | 0.058422 | 0.035603 | (cal/cm^2) | #VALUE! | 0.11056 | 0.060992
|  |  | 8 | 1557
|  |  | 6 | 2425 |  |  |  | E | #VALUE! |  | 35.5578 | 21.6691 | (J/cm^2) | #VALUE! | 67.2914 | 37.1221
|  |  | 4 | 3806 |  |  |  | E | #VALUE! |  | 8.5271 | 5.1964 | (cal/cm^2) | #VALUE! | 16.137 | 8.9022
|  |  | 3 | 4774 |  |  |  | E (calculation factor) (9.11.3) | #VALUE! |  | 12.7906 | 7.7946 |  | #VALUE! | 24.2055 | 13.3533
|  |  | 2 | 5907
|  |  | 1 | 7293
|  |  | 1/0 | 8925
|  |  | 2/0 | 10755